## Sheet1
Component | Parameter | Value | Unit | Source
Solar Photovoltaic | Nominal capacity | 1,000 | kW | Site assumption
Solar Photovoltaic | Tilt angle | 35 | ° | Site assumption
Solar Photovoltaic | Azimuth | 180 | ° | Site assumption
Solar Photovoltaic | Temperature coeff. | -0.4 | %/°C | pvlib default
Battery Storage (BESS) | Power rating | 500 | kW | 4-hr duration
Battery Storage (BESS) | Energy capacity | 2,000 | kWh | 4-hr duration
Battery Storage (BESS) | Charge efficiency | 95 | % | Manufacturer
Battery Storage (BESS) | Discharge eff. | 95 | % | Manufacturer
Battery Storage (BESS) | Round-trip eff. | 90.25 | % | Computed
Battery Storage (BESS) | Standing loss | 0.02 | %/hr | Literature
PCM Thermal Storage | Power rating | 200 | kW | 8-hr duration
PCM Thermal Storage | Energy capacity | 1,600 | kWh | 8-hr duration
PCM Thermal Storage | Charge efficiency | 95 | % | Paraffin PCM
PCM Thermal Storage | Discharge eff. | 92 | % | Paraffin PCM
PCM Thermal Storage | Round-trip eff. | 87.4 | % | Computed
PCM Thermal Storage | Standing loss | 0.1 | %/hr | Literature
Electrolyser (PEM) | Input power | 200 | kW | Sized for surplus
Electrolyser (PEM) | LHV efficiency | 70 | % | Current PEM
Electrolyser (PEM) | Marginal cost | 1 | £/MWh | O&M
Hydrogen Tank | Energy capacity | 5,000 | kWh | Seasonal sizing
Hydrogen Tank | Standing loss | 0.01 | %/hr | Literature
Fuel Cell (PEM) | Output power | 100 | kW | Backup supply
Fuel Cell (PEM) | LHV efficiency | 50 | % | Current PEM
Fuel Cell (PEM) | Marginal cost | 2 | £/MWh | O&M
Fuel Cell (PEM) | H2 round-trip | 35 | % | Computed
Heat Pump | Power rating | 300 | kW | Site sizing
Heat Pump | Seasonal COP | 3.0 | - | Air-source
Heat Pump | Marginal cost | 0.5 | £/MWh | O&M
Backup Boiler | Thermal capacity | 600 | kW | Site sizing
Backup Boiler | Marginal cost | 110 | £/MWh | UK gas 2024
Grid Connection | Import capacity | 2,000 | kW | Site limit
Grid Connection | Export capacity | 500 | kW | Export agreement
Grid Connection | Import tariff | 280 | £/MWh | UK 2024
Grid Connection | Export tariff | 50 | £/MWh | SEG
Grid Connection | Carbon intensity | 0.233 | kgCO2/kWh | NG ESO 2023
Site Demand | Peak electrical | 681 | kW | CIBSE
Site Demand | Annual electrical | 1,816 | MWh | CIBSE
Site Demand | Peak thermal | 755 | kW | CIBSE
Site Demand | Annual thermal | 1,648 | MWh | CIBSE